## Readme
This workbook provides a summary of each the generic resource costs extracted from technical sources documented in 2021 NREL Annual Technology Baseline cost report which are relevant to options to be considered in the 2023 Electric Progress Report portfolio planning process.
Objective
The objective of this document is to provide an organized accounting of potential Generic Resource costs pulled from the various technical sources available from the 2021 NREL ATB cost methodology page in order to better understand how specific cost components effect total Generic Resource costs.
List of resources examined
| Category | Resource Type | Description of included information
Renewable
|  | Offshore Wind | Cost, operating characteristic data & relevant source maps
|  | Onshore Wind | Cost, operating characteristic data
Battery Hybrid
|  | Solar + | Cost & operating characteristic data for utility & residential scale solar. With and without battery hybrid.
Storage
|  | Batteries | Cost data across various battery technologies, sizes & and discharging widows
|  | Pumped Hydro Storage | Cost data
Thermal
|  | CCCT | Cost, operating characteristic data for configurations with & without carbon capture
|  | Recip Peaker | Cost, operating characteristic data
|  | Frame Peaker | Cost, operating characteristic data
|  | Biomass | Cost, operating characteristic data
Emerging Technology
|  | Small Modular Nuclear | Cost, operating characteristic data
Definitions
| Capital Cost | Capital expenditures required to achieve commercial operation of the generation plant. This document attempts to present a reasonable breakdown of capital cost into components such as equipment, balance of plant, engineer, procure, construct, and other costs based on source material provided as part of the 2021 NREL ATB.
| BOP/BOS | Balance of Plant/Balance of System
| PV | Photo Voltaic
| LI | Lithium Ion
| HHV/LHV | Higher Heating Value/Lower Heating Value
| CAPEX | Capital expenditures accrued in construction of resource
Notes
Values listed in currency year in native sources and converted to 2020 dollars
Detailed source information can be found in Metadata sheet
Cost comparison across resources can be found in CC Matrix sheet

## Metadata
Sources, gathered from 2021 NREL ATB cost report
|  |  | Reference ID | Publication Date | Title | Authors | URL
|  |  | A | 2016 | A Spatial-Economic CostReduction Pathway Analysis for U.S. Offshore Wind Energy Development from 2015–2030 | Philipp Beiter, Walter Musial, Aaron Smith, Levi Kilcher, Rick Damiani, Michael Maness, Senu Sirnivas, Tyler Stehly, Vahan Gevorgian, Meghan Mooney, and George Scott National Renewable Energy Laboratory | https://www.nrel.gov/docs/fy16osti/66579.pdf
|  |  | B | 2019 | 2019 Cost of Wind Energy Review | Tyler Stehly, Philipp Beiter, and Patrick Duffy National Renewable Energy Laboratory | https://www.nrel.gov/docs/fy21osti/78471.pdf
|  |  | C | 2020 | Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies | Sargent & Lundy for EIA | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
|  |  | D | 2019 | COST AND PERFORMANCE BASELINE FOR FOSSIL ENERGY PLANTS VOLUME 1: BITUMINOUS COAL AND NATURAL GAS TO ELECTRICITY | National Energy Technology Laboratory (NETL) - Robert James, Mission Execution and Strategic Analysis (MESA) - Alexander Zoelle, Dale Keairns, Marc Turner, Mark Woods, Norma Kuehn | https://www.netl.doe.gov/projects/files/CostAndPerformanceBaselineForFossilEnergyPlantsVol1BitumCoalAndNGtoElectBBRRev4-1_092419.pdf
|  |  | E | 2020 | U.S. Solar Photovoltaic System and Energy Storage Cost Benchmark: Q1 2020 | David Feldman, Vignesh Ramasamy, Ran Fu, Ashwin Ramdas, Jal Desai, and Robert Margolis National Renewable Energy Laboratory | https://www.nrel.gov/docs/fy21osti/77324.pdf
|  |  | F | 2020 | 2020 Grid Energy Storage Technology Cost and Performance Assessment | Kendall Mongird, Vilayanur Viswanathan, Jan Alam, Charlie Vartanian, Vincent Sprenkle*, Pacific Northwest National Laboratory. Richard Baxter, Mustang Prairie Energy | https://www.pnnl.gov/sites/default/files/media/file/Final%20-%20ESGC%20Cost%20Performance%20Report%2012-11-2020.pdf
https://www.pnnl.gov/lithium-ion-battery-lfp-and-nmc
https://www.pnnl.gov/vanadium-redox-flow-battery
Resource type | size/config
|  | currency year | References used
offshore wind | fixed |  | A, B
offshore wind | floating | 2015, 2019 | A, B
onshore wind |  | 2019 | B
frame peaker |  | 2019 | C
recip peaker |  | 2019 | C
NGCC | w/ capture | 2018 | D
NGCC | w/o capture | 2018 | D
Batteries | .5 hour | 2019, 2020 | B, F
Batteries | 1 hour | 2019, 2020 | B, F
Batteries | 2 hour | 2019, 2020 | B, F
Batteries | 4 hour | 2019, 2020 | B, F
battery + PV | DC-coupled, colocated | 2019 | B
battery + PV | AC-coupled, colocated | 2019 | B
battery + PV | in Different States | 2019 | B
Pumped Hydro |  | 2020 | F
Biomass |  | 2019 | C
Small mod nuclear |  | 2019 | C
Resources List in NREL ATB Report
CCCT
Frame Peaker
Recip Peaker
Solar Utility
Solar Residential
Onshore Wind - WA
Onshore Wind - MT
Onshore Wind - ID/WY
Offshore Wind
Pumped Storage
Battery (4hr, Li-Ion)
Battery (2hr, Li-Ion)
Battery (4hr, Flow)
Battery (6hr, Flow)
Solar + Battery
Wind + Battery
Biomass
Wind + PSEH
Inflation rate by Year | bls.gov | FRED via Worldbank | BEA | mean
2016 | 2.1% | 1.26% | 1% | 1.453%
2017 | 2.1% | 2.13% | 1.9% | 2.043%
2018 | 1.9% | 2.44% | 2.4% | 2.247%
2019 | 2.3% | 1.81% | 1.8% | 1.97%
2020 | 1.4% | 1.23% | 1.3% | 1.31%

## Offshore wind
source: https://www.nrel.gov/docs/fy16osti/66579.pdf |  |  |  | Source: https://www.nrel.gov/docs/fy21osti/78471.pdf | [5 empty] | Source: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
Estimates made for 100 unit order, include 5 yr warranty, & delivery to staging port |  |  |  | Native 2019 $ | [5 empty] | 2019 $
Table 5 | Cost ($/kW) | total cost for 6MW turbine |  |  | fixed bottom | floating bottom | fixed bottom |  |  | Configuration | Fixed-bottom Monopile foundations 400MW
Turbine | 1583 | 9498000 |  |  | 6.1 MW |  |  |  |  | Offshore cable length (miles) | 30
Development | 196 | 1176000 |  | Turbine capital costs | $/kW | $/kW | $/1000 |  |  | Onshore cable length (miles) | 5
Ports & Staging | 25 | 150000 |  | total | 1301 | 1301 | 7936.1 |  |  | Water depth (ft) | 100
Operations | 31 | 186000 |  | Balance of System |  |  | 0 |  |  | Cost Components | Thousands $
Total |  | 11010000 |  | Development | 138 | 165 | 841.8 |  |  | Civil/Structural/Architectural subtotal | 240648
|  |  |  | Engineering & Mgmt | 70 | 85 | 427 |  |  | WTG Procurement & supply | 653008
| Factor |  |  | Substructure & foundation | 817 | 1438 | 4983.7 |  |  | WTG Assembly/installation | 125792
Engineering & Mgmt | 3.5% of all CAPEX |  |  | Port & staging,logistics,transport | 58 | 44 | 353.8 |  |  | Mechanical subtotal | 778800
Insurance During Construction | 1% of all CAPEX |  |  | electrical infrastructure | 761 | 979 | 4642.1 |  |  | Interconnection | 60995
Commisioning | 1% of all CAPEX |  |  | Assembly & installation | 198 | 439 | 1207.8 |  |  | Offshore transmission & eBOP | 213947
Installation Contingency | 30% installation CAPEX |  |  | Lease price | 88 | 88 | 536.8 |  |  | Onshore transmission | 60182
Procurement Contingency | 5% non-installation CAPEX |  |  | Total | 2131 | 3237 | 12999.1 |  |  | Electrical subtotal | 335114
Decommissioning | 15% Installation CAPEX |  |  | Soft Costs |  |  | 0 |  |  | Project indirects | 74800
|  |  |  | Insurance during construction | 44 | 52 | 268.4 |  |  | EPC Fee | 85762
Fixed Component Build Cost* | cost / t (USD) | Table 8 |  | Decommissioning bond | 58 | 76 | 353.8 |  |  | EPC subtotal | 1515124
Pile | 2250 |  |  | construction financing | 183 | 221 | 1116.3 |  |  | Owner's cost | 75756.2
Monopile Transition Piece | 3230 |  |  | contingency | 316 | 389 | 1927.6 |  |  | Project contingency | 159088
Jacket Main Lattice Structure | 4680 |  |  | Plant commissioning | 44 | 52 | 268.4 |  |  | Total CAPEX | 1749968.2
Jacket Transition Piece | 4599 |  |  | Total | 645 | 790 | 3934.5
Total Fixed CC | 14759 |  |  | Total CAPEX | 4077 | 5328 | 24869.7 |  |  | Fixed O&M ($/kW-yr) | 110
|  |  |  | OpEx | 124/year | 130/year
Floating Component Costs |  | Table 9 |  | Net CF | 0.488 | 0.38
Stiffened Column | 3120 | [8 empty] | Configuration | Fixed bottom: monopile foundations 400MW ¦ 10MW WTG
Tapered Column | 4220 | [8 empty] | offshore cable length (miles) | 30
Truss Members | 6250 | [8 empty] | Onshore cable length (miles) | 5
Heave Plate | 5250 | [8 empty] | water depth (ft) | 100
Outfitting | 7250 | [8 empty] | Emissions | N/A
Fixed Ballast | 150
Total Floating CC | 26240
Via Figure A-8 | $/MW/mile | $/kW/mile
Regional Spur Line (230kV) | 3,751 - 4,000 | 3875500 | 635.3279
*reffers to build costs which don't vary with turbine size
costs listed in 2015 dollars
modeled for year 2015
|  |  |  | Adjusted to 2020 $ | [5 empty] | Adjusted to 2020 $
[5 empty] | fixed bottom | floating bottom | fixed bottom | Operating characteristics and specs |  | Configuration | Fixed-bottom Monopile foundations 400MW
[5 empty] | 6.1 MW |  |  | Turbine rated power (MW) | 6.1 | Offshore cable length (miles) | 30
|  |  |  | Turbine capital costs | $/kW | $/kW | $/1000 | Turbine rotor diameter (m) | 150.7 | Onshore cable length (miles) | 5
|  |  |  | total | 1326.6297 | 1326.6297 | 8092.4412 | Turbine height (m) | 101.8 | Water depth (ft) | 100
|  |  |  | Balance of System |  |  |  | Max rotor tip speed (m/s) | 80 | Cost Components | Thousands $
|  |  |  | Development | 140.7186 | 168.2505 | 858.3835 | Project design life (yrs) | 25 | Civil/Structural/Architectural subtotal | 245388.7656
|  |  |  | Engineering & Mgmt | 71.379 | 86.6745 | 435.4119 | Drivetrain design | geared | WTG Procurement & supply | 665872.2576
|  |  |  | Substructure & foundation | 833.0949 | 1466.3286 | 5081.8789 | Cut-in wind speed (m/s) | 3 | WTG Assembly/installation | 128270.1024
|  |  |  | Port & staging,logistics,transport | 59.1426 | 44.8668 | 360.7699 | Cut-out wind speed (m/s) | 25 | Mechanical subtotal | 794142.36
|  |  |  | electrical infrastructure | 775.9917 | 998.2863 | 4733.5494 | Max coefficient of power | 0.47 | Interconnection | 62196.6015
|  |  |  | Assembly & installation | 201.9006 | 447.6483 | 1231.5937 | Annual mean wind speed at 50m (m/s) | 7.67 | Offshore transmission & eBOP | 218161.7559
|  |  |  | Lease price | 89.7336 | 89.7336 | 547.375 | Annual mean wind speed at 101.8 m (m/s) | 8.3 | Onshore transmission | 61367.5854
|  |  |  | Total | 2172.9807 | 3300.7689 | 13255.1823 | Weibull k | 2.1 | Electrical subtotal | 341715.7458
|  |  |  | Soft Costs |  |  |  | Shear exponent | 0.1 | Project indirects | 76273.56
|  |  |  | Insurance during construction | 44.8668 | 53.0244 | 273.6875 |  |  | EPC Fee | 87451.5114
|  |  |  | Decommissioning bond | 59.1426 | 77.4972 | 360.7699 | Losses | 20.9% | EPC subtotal | 1544971.9428
|  |  |  | construction financing | 186.6051 | 225.3537 | 1138.2911 | Availability | 98% | Owner's cost | 77248.5971
|  |  |  | contingency | 322.2252 | 396.6633 | 1965.5737 | Net energy capture (MWh/MW/year) | 3328 | Project contingency | 162222.0336
|  |  |  | Plant commissioning | 44.8668 | 53.0244 | 273.6875 | Net capacity factor | 38% | Total CAPEX | 1784442.5735
|  |  |  | Total | 657.7065 | 805.563 | 4012.0096
|  |  |  | Total CAPEX | 4157.3169 | 5432.9616 | 25359.6331
Relevant Charts from Source Material | source: https://www.nrel.gov/docs/fy16osti/66579.pdf
Figure 12. Estimated excluded areas due to competing use and environmental exclusions. Image from Black & Veatch (2010) |  |  |  | Figure 27. Construction and operations port and inshore assembly area locations

## Onshore wind
Source: https://www.nrel.gov/docs/fy21osti/78471.pdf |  | Table 4 | Operating characteristics and specs
Native 2019 $ | Size |  | Turbine rated power (MW) | 2.6
Cost Component | 2.6MW |  | Turbine rotor diameter (m) | 121.2
Turbine capital cost | $/kW | $ | Turbine height (m) | 90.1
Rotor module | 287 | 746200 | Max rotor tip speed (m/s) | 80
Nacelle module | 488 | 1268800 | Number of turbines | 79
Tower module | 215 | 559000 | Wind plant capacity (MW) | 200
total | 991 | 2576600 | Altitude about mean sea level | 450
Balance of System |  | 0 | Project design life (yrs) | 25
Dev cost | 16 | 41600 | Drivetrain design | geared
Engineering & Mgmt | 18 | 46800 | Cut-in wind speed (m/s) | 3
Foundation | 59 | 153400 | Cut-out wind speed (m/s) | 25
Site access & staging | 44 | 114400 | Max coefficient of power | 0.47
Assembly & installation | 44 | 114400 | Annual mean wind speed at 50m | 7.25
electrical infrastructure | 145 | 377000 | Annual mean wind speed at 90.1 m | 7.89
Total | 326 | 847600 | Weibull k | 2
financial costs |  | 0 | Shear exponent | 0.143
Construction financing | 34 | 88400
Contingency fund | 86 | 223600 | Losses | 15%
Total | 120 | 312000 | Availability | 98%
Total CAPEX | 1436 | 3733600 | Net energy capture (MWh/MW/year) | 3734
Net CF | 0.426 |  | Net capacity factor | 42.6%
OpEx | 43/year
Adjusted to 2020 $ | Size
Cost Component | 2.6MW
Turbine capital cost | $/kW | 2020$
Rotor module | 292.6539 | 760900.14
Nacelle module | 497.6136 | 1293795.36
Tower module | 219.2355 | 570012.3
total | 1010.5227 | 2627359.02
Balance of System |  | 0
Dev cost | 16.3152 | 42419.52
Engineering & Mgmt | 18.3546 | 47721.96
Foundation | 60.1623 | 156421.98
Site access & staging | 44.8668 | 116653.68
Assembly & installation | 44.8668 | 116653.68
electrical infrastructure | 147.8565 | 384426.9
Total | 332.4222 | 864297.72
financial costs |  | 0
Construction financing | 34.6698 | 90141.48
Contingency fund | 87.6942 | 228004.92
Total | 122.364 | 318146.4
Total CAPEX | 1464.2892 | 3807151.92

## Solar +
source: | https://www.nrel.gov/docs/fy21osti/77324.pdf
Native 2019 $
| Source: Table 21 |  |  |  |  | Source: Figure 30 |  | Source: Figure 37
| All listings for 100MW PV + 60MW Battery; Utility |  |  |  |  | Configuration | 100MW dc single axis tracking | Residential PV, storage |  | 7kW PV + DC coupled 3kW battery | 7kW PV + AC coupled 3kW battery | 7kW PV + DC coupled 5kW battery | 7kW PV + AC coupled 5kW battery
| Configuration | DC-coupled, colocated | AC-coupled, colocated | in Different States |  | Module component | Cost in $, rough | Configuration | 7kW PV
| Module Components | Cost in $ |  |  |  | Module | 41000000 | Cost components | $ | $ | $ | $ | $
| PV module | 40587666 | 40587666 | 40587666 |  | Inverter | 5000000 | PV modules | 2844 | 2844 | 2844 | 2844 | 2844
| LI-ion Battery | 46091749 | 46091749 | 46091749 |  | Structural BOS | 12000000 | Lithium-ion battery | 0 | 1503 | 1503 | 5009 | 5009
| Solar interver |  | 5171344 | 5171344 |  | Electrical BOS | 7000000 | PV inverter | 1754 | 0 | 1754 | 0 | 1754
| Bidirectional inverter | 3563795 | 3563795 | 3563795 |  | Total BOS | 19000000 | Battery inverter | 0 | 1034 | 1034 | 3445 | 3445
| Structural BOS | 15908348 | 15289203 | 15342164 |  | Install labor & equipment | 11000000 | Structural BOS | 589 | 589 | 589 | 589 | 589
| Electrical BOS | 13384607 | 10336576 | 15855408 |  | EPC overhead | 6000000 | Electrical BOS | 1600 | 3060 | 2755 | 3060 | 2755
| Install. Labor & equip. | 15537385.79 | 13417123.8 | 15757821 |  | Sales tax | 4000000 | Supply chain costs | 1825 | 2042 | 2025 | 2338 | 2321
| EPC overheard | 7905594 | 6826782 | 8017754 |  | Total EPC | 86000000 | Sales tax | 440 | 724 | 704 | 1079 | 1059
| Sales Tax at 5% | 7645117 | 7741319 | 8097671 |  | Land |  | Installed Labor & equipment | 1309 | 1994 | 2252 | 2080 | 2424
| Total EPC | 150624261.79 | 149025557.8 | 158485372 |  | Permitting fee |  | Permitting, inspection, interconnection | 1668 | 1668 | 1668 | 1668 | 1668
| Land acquisition | 0 | 0 | 0 |  | Interconnection fee | 3000000 | Sales & Marketing | 2996 | 5238 | 5496 | 6446 | 6704
| Permitting fee | 198395 | 198395 | 396790 |  | Transmission line | 2000000 | Net profit | 2045 | 1874 | 2164 | 2895 | 3199
| Interconnection fee | 2784560 | 2784560 | 5569120 |  | Developer overhead | 2000000 | Calculated Total | 17070 | 22570 | 24788 | 31453 | 33771
| Transmission line | 1669331 | 1669331 | 1669331 |  | Contingency | 3000000 | Reported total | 18990 | 26153 | 28371 | 35591 | 37909
| Contingency | 4658296 | 4610335 | 4980515 |  | EPC/developer profit | 5000000
| Developer overhead | 4658296 | 4610335 | 3523821 |  | Developer cost | 15000000
| EPC/developer profit | 8229657 | 8144926 | 8688259 |  | Total | 101000000
| Developer cost | 22198535 | 22017882 | 24827836 |  | O&M Expenses ($/kW-yr) | 17
| Total energy storage system cost | 172822796.79 | 171043439.8 | 183313208
Updated to 2020 $
| Source: Table 21 |  |  |  |  | Source: Figure 30 |  | Residential PV, storage |  | 7kW PV + DC coupled 3kW bat | 7kW PV + AC coupled 3kW battery | 7kW PV + DC coupled 5kW battery | 7kW PV + AC coupled 5kW battery | Ave 7kW with battery
| All listings for 100MW PV + 60MW Battery; Utility |  |  |  |  | Configuration | 100MW dc single axis tracking | Configuration | 7kW PV
| Configuration | DC-coupled, colocated | AC-coupled, colocated | in Different States | Average | Module component | Cost in $, rough | Cost components
| Module Components | Cost in $ |  |  | $/1000 | Module | 44977000 | PV modules | 3119.868 | 3119.868 | 3119.868 | 3119.868 | 3119.868 | 3119.868
| PV module | 44524669.602 | 44524669.602 | 44524669.602 | 44524.6696 | Inverter | 5485000 | Lithium-ion battery | 0 | 1648.791 | 1648.791 | 5494.873 | 5494.873 | 3571.832
| LI-ion Battery | 50562648.653 | 50562648.653 | 50562648.653 | 50562.6487 | Structural BOS | 13164000 | PV inverter | 1924.138 | 0 | 1924.138 | 0 | 1924.138 | 962.069
| Solar interver | 0 | 5672964.368 | 5672964.368 | 3781.9762 | Electrical BOS | 7679000 | Battery inverter | 0 | 1134.298 | 1134.298 | 3779.165 | 3779.165 | 2456.7315
| Bidirectional inverter | 3909483.115 | 3909483.115 | 3909483.115 | 3909.4831 | Total BOS | 20843000 | Structural BOS | 646.133 | 646.133 | 646.133 | 646.133 | 646.133 | 646.133
| Structural BOS | 17451457.756 | 16772255.691 | 16830353.908 | 17018.0225 | Install labor & equipment | 12067000 | Electrical BOS | 1755.2 | 3356.82 | 3022.235 | 3356.82 | 3022.235 | 3189.5275
| Electrical BOS | 14682913.879 | 11339223.872 | 17393382.576 | 14471.8401 | EPC overhead | 6582000 | Supply chain costs | 2002.025 | 2240.074 | 2221.425 | 2564.786 | 2546.137 | 2393.1055
| Install. Labor & equip. | 17044512.2116 | 14718584.8086 | 17286329.637 | 16349.8089 | Sales tax | 4388000 | Sales tax | 482.68 | 794.228 | 772.288 | 1183.663 | 1161.723 | 977.9755
| EPC overheard | 8672436.618 | 7488979.854 | 8795476.138 | 8318.9642 | Total EPC | 94342000 | Installed Labor & equipment | 1435.973 | 2187.418 | 2470.444 | 2281.76 | 2659.128 | 2399.6875
| Sales Tax at 5% | 8386693.349 | 8492226.943 | 8883145.087 | 8587.3551 | Land | 0 | Permitting, inspection, interconnection | 1829.796 | 1829.796 | 1829.796 | 1829.796 | 1829.796 | 1829.796
| Total EPC | 165234815.1836 | 163481036.9066 | 173858453.084 | 167524.7684 | Permitting fee | 0 | Total | 18725.79 | 24759.29 | 27192.436 | 34503.941 | 37046.787 | 30875.6135
| Land acquisition | 0 | 0 | 0 | 0 | Interconnection fee | 3291000
| Permitting fee | 217639.315 | 217639.315 | 435278.63 | 290.1858 | Transmission line | 2194000
| Interconnection fee | 3054662.32 | 3054662.32 | 6109324.64 | 4072.8831 | Developer overhead | 2194000
| Transmission line | 1831256.107 | 1831256.107 | 1831256.107 | 1831.2561 | Contingency | 3291000
| Contingency | 5110150.712 | 5057537.495 | 5463624.955 | 5210.4377 | EPC/developer profit | 5485000
| Developer overhead | 5110150.712 | 5057537.495 | 3865631.637 | 4677.7733 | Developer cost | 16455000
| EPC/developer profit | 9027933.729 | 8934983.822 | 9531020.123 | 9164.6459 | Total | 110797000
| Developer cost | 24351792.895 | 24153616.554 | 27236136.092 | 25247.1818 | O&M Expenses ($/kW-yr) | 18.649
| Total energy storage system cost | 189586608.0786 | 187634653.4606 | 201094589.176 | 192771.9502
Operating Characteristics
PV systems quoted in DC terms
PV (solar) | annual degradation | 0.5% - 0.7%
| System losses - preintervter derate | 9.5%
| System losses - inverter efficiency | 2%
| Utility scale inverter | 1500 V
| inverter loading ratio (2020) | 1.34
Residential PV + Battery
| inverter | 6-8 kW 48V bidirectional
| assumed depth of discharge | 80%
| assumed efficiency | 90%
| 10yr schedule for bat, inv replacement | 20% replacement rate
| 20yr schedule for bat, inv replacement | 20% replacement rate
| % of generation fed to bat. | 25% - 33% | Asumes a 75% discharge per day for a 2-hr 3 kW battery
| O&M ($/kW/yr) | 39
| roudtrip energy losses | 8% - 10%
| system lifetime (years) | 30
Utility PV + Battery
| % of generation fed to bat. | 30% - 42% | Asumes a 75% discharge per day for a 4-hr 60 MW battery
| roudtrip energy losses | 8% - 10%
| Degradation | 0.7%
| O&M ($/kW/yr) | 27 | Assumes storage O&M add $10/kW-yr to PV costs
| system lifetime (years) | 30

## Batteries
Native 2019 $
| Lithium Ion Source: https://www.nrel.gov/docs/fy21osti/77324.pdf | [5 empty] | Lead Acid & Vanadium Flow Source: https://www.pnnl.gov/sites/default/files/media/file/Final%20-%20ESGC%20Cost%20Performance%20Report%2012-11-2020.pdf | [15 empty] | Additional info from this source at: https://www.pnnl.gov/lithium-ion-battery-lfp-and-nmc | [6 empty] | And https://www.pnnl.gov/vanadium-redox-flow-battery | https://www.nrel.gov/docs/fy21osti/78694.pdf
| Source: Table 18 | [5 empty] | Lead Acid Batteries | [6 empty] | Vanadium Batteries | [8 empty] | Lithium Ion Batteries (LFP) | [7 empty] | Residential Batteries - Lithium Ion - Storage Only-AC Coupled
| Lithium Ion Batteries | [5 empty] | Size | 1MW |  | 10MW |  | 100MW |  | Size | 1MW |  | 10MW |  | 100MW |  |  |  | Size |  | 10 MW |  |  | 100 MW |  |  | Size | 5 kW
| Size | 60 MW |  |  |  |  | Duration (hours) | 4 | 10 | 4 | 10 | 4 | 10 | Duration (hours) | 4 | 10 | 4 | 10 | 2 | 4 | 6 | 10 | Duration (hours) | 2 | 4 | 6 | 2 | 4 | 6 |  | Duration (hours) | 2.5 hrs (14 kwH)
| Duration | 4 hour | 2 hour | 1 hour | .5 hour |  | Module Components Cost in $ | $/kW | [5 empty] | Module Components Cost in $ | $/kW |  | $/kW |  | $/kW |  |  |  | Module Components | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW |  | Module Components
| Module Components Cost in $ | [5 empty] | Storage Block | 720 | 1800 | 684 | 1710 | 648 | 1620 | Storage Block | 1156 | 2310 | 1100 | 2200 | 696 | 1044 | 1392 | 2090 | Storage Block | 352 | 696 | 1032 | 336 | 660 | 984 |  | Lithium Ion Battery | 3479
| LI-ion Battery | 46560000 | 23760000 | 13380000 | 7260000 |  | Storage balance of system | 196 | 490 | 188 | 470 | 180 | 450 | Storage balance of system | 232 | 460 | 220 | 440 | 140 | 208 | 276 | 420 | Storage balance of system | 86 | 160 | 234 | 82 | 152 | 222 |  | Battery Inverter | 2393
| Battery central inverter | 3600000 | 3600000 | 3600000 | 3600000 |  | Power Equipment | 155 | 155 | 133 | 133 | 115 | 115 | Power Equipment | 155 | 155 | 133 | 133 | 115 | 115 | 115 | 115 | Power Equipment | 73 | 73 | 73 | 63 | 63 | 63 |  | Electrical BOS | 1507
| Structural BOS | 3173302 | 1853216 | 1193174 | 863152 |  | Controls & communication | 40 | 40 | 8 | 8 | 2 | 2 | Controls & communication | 40 | 40 | 8 | 8 | 2 | 2 | 2 | 2 | Controls & communication | 8 | 8 | 8 | 2 | 2 | 2 |  | Suuply Chain Costs | 369
| Electrical BOS | 8599517 | 6087485 | 4831469 | 4203461 |  | System integration | 188 | 430 | 176 | 410 | 164 | 390 | System integration | 220 | 430 | 204 | 400 | 132 | 192 | 168 | 380 | System integration | 104 | 188 | 270 | 96 | 176 | 252 |  | Sales Tax | 535
| Install. Labor & equip. | 4694348 | 3706099 | 3211975 | 2964913 |  | Eng., procurement, construction | 208 | 470 | 196 | 450 | 184 | 430 | Eng., procurement, construction | 252 | 500 | 232 | 460 | 152 | 216 | 192 | 430 | Eng., procurement, construction | 124 | 224 | 324 | 116 | 212 | 306 |  | Install Labor and Equipment | 1560
| EPC overheard | 2354557 | 1623195 | 1257513 | 1074673 |  | Project Dev | 268 | 610 | 248 | 570 | 232 | 540 | Project Dev | 320 | 640 | 292 | 590 | 184 | 272 | 240 | 540 | Project Dev | 150 | 268 | 390 | 140 | 252 | 366 |  | Permitting, Inspection, Interconnection | 1209
| Sales Tax at 5% | 3807403 | 2236341 | 1509970 | 1092844 |  | Grid integration | 31 | 31 | 25 | 25 | 20 | 20 | Grid integration | 31 | 31 | 25 | 25 | 20 | 20 | 20 | 20 | Grid integration | 25 | 25 | 25 | 20 | 20 | 20 |  | Overhead | 1940
| Total EPC | 72789127 | 42866336 | 28984101 | 21059043 |  | Total ESS intalled cost | 1806 | 4026 | 1658 | 3776 | 1545 | 3567 | Total ESS intalled cost | 2406 | 4566 | 2214 | 4256 | 1438 | 2069 | 2710 | 3997 | Total ESS intalled cost | 922 | 1643 | 2355 | 854 | 1541 | 2220 |  | Sales and Marketing | 3829
| Land acquisition | 0 | 0 | 0 | 0 | [25 empty] | Net Profit | 1920
| Permitting fee | 295289 | 295289 | 295289 | 295289 | [25 empty] | TOTAL | 18741
| Interconnection fee | 1849475 | 1849475 | 1849475 | 1849475
| Contingency | 2265878 | 1359264 | 938331 | 698347 |  | 776 | 396
| Developer overhead | 1603157 | 961708 | 663889 | 494095 | [19 empty] | 358
| EPC/developer profit | 3940146 | 2366604 | 1636554 | 1219812
| Developer cost | 9953945 | 6832340 | 5383538 | 4557018
| Total energy storage system cost | 82743072 | 49698676 | 34367639 | 25616061
Updated to 2020 $
| Source: Table 18 | [5 empty] | Lead Acid Batteries | [6 empty] | Vanadium Batteries
| All listings for 60MW LI batteries | [5 empty] | Size | 1MW |  | 10MW |  | 100MW |  | Size | 1MW |  | 10MW |  | 100MW
| Size | 4 hour | 2 hour | 1 hour | .5 hour |  | Duration (hours) | 4 | 10 | 4 | 10 | 4 | 10 | Duration (hours) | 4 | 10 | 4 | 10 | 2 | 4 | 6 | 10
| Module Components Cost in $ | [5 empty] | Module Components Cost in $ | $/kW | [5 empty] | Module Components Cost in $ | $/kW |  | $/kW |  | $/kW
| LI-ion Battery | 47477232 | 24228072 | 13643586 | 7403022 |  | Storage Block | 734.184 | 1835.46 | 697.4748 | 1743.687 | 660.7656 | 1651.914 | Storage Block | 1268.132 | 2534.07 | 1206.7 | 2413.4 | 763.512 | 1145.268 | 1527.024 | 2292.73
| Battery central inverter | 3670920 | 3670920 | 3670920 | 3670920 |  | Storage balance of system | 199.8612 | 499.653 | 191.7036 | 479.259 | 183.546 | 458.865 | Storage balance of system | 254.504 | 504.62 | 241.34 | 482.68 | 153.58 | 228.176 | 302.772 | 460.74
| Structural BOS | 3235816.0494 | 1889724.3552 | 1216679.5278 | 880156.0944 |  | Power Equipment | 158.0535 | 158.0535 | 135.6201 | 135.6201 | 117.2655 | 117.2655 | Power Equipment | 170.035 | 170.035 | 145.901 | 145.901 | 126.155 | 126.155 | 126.155 | 126.155
| Electrical BOS | 8768927.4849 | 6207408.4545 | 4926648.9393 | 4286269.1817 |  | Controls & communication | 40.788 | 40.788 | 8.1576 | 8.1576 | 2.0394 | 2.0394 | Controls & communication | 43.88 | 43.88 | 8.776 | 8.776 | 2.194 | 2.194 | 2.194 | 2.194
| Install. Labor & equip. | 4786826.6556 | 3779109.1503 | 3275250.9075 | 3023321.7861 |  | System integration | 191.7036 | 438.471 | 179.4672 | 418.077 | 167.2308 | 397.683 | System integration | 241.34 | 471.71 | 223.788 | 438.8 | 144.804 | 210.624 | 184.296 | 416.86
| EPC overheard | 2400941.7729 | 1655171.9415 | 1282286.0061 | 1095844.0581 |  | Eng., procurement, construction | 212.0976 | 479.259 | 199.8612 | 458.865 | 187.6248 | 438.471 | Eng., procurement, construction | 276.444 | 548.5 | 254.504 | 504.62 | 166.744 | 236.952 | 210.624 | 471.71
| Sales Tax at 5% | 3882408.8391 | 2280396.9177 | 1539716.409 | 1114373.0268 |  | Project Dev | 273.2796 | 622.017 | 252.8856 | 581.229 | 236.5704 | 550.638 | Project Dev | 351.04 | 702.08 | 320.324 | 647.23 | 201.848 | 298.384 | 263.28 | 592.38
| Total EPC | 74223072.8019 | 43710802.8192 | 29555087.7897 | 21473906.1471 |  | Grid integration | 31.6107 | 31.6107 | 25.4925 | 25.4925 | 20.394 | 20.394 | Grid integration | 34.007 | 34.007 | 27.425 | 27.425 | 21.94 | 21.94 | 21.94 | 21.94
| Land acquisition | 0 | 0 | 0 | 0 |  | Total ESS intalled cost | 1841.5782 | 4105.3122 | 1690.6626 | 3850.3872 | 1575.4365 | 3637.2699 | Total ESS intalled cost | 2639.382 | 5008.902 | 2428.758 | 4668.832 | 1577.486 | 2269.693 | 2972.87 | 4384.709
| Permitting fee | 301106.1933 | 301106.1933 | 301106.1933 | 301106.1933
| Interconnection fee | 1885909.6575 | 1885909.6575 | 1885909.6575 | 1885909.6575
| Contingency | 2310515.7966 | 1386041.5008 | 956816.1207 | 712104.4359
| Developer overhead | 1634739.1929 | 980653.6476 | 676967.6133 | 503828.6715
| EPC/developer profit | 4017766.8762 | 2413226.0988 | 1668794.1138 | 1243842.2964
| Developer cost | 10150037.7165 | 6966937.098 | 5489593.6986 | 4646791.2546
| Total energy storage system cost | 84373110.5184 | 50677739.9172 | 35044681.4883 | 26120697.4017
| Average Battery | 100MW
| size | 4 | 10
Duration (hours)
Cost in $/1000
| Storage Block | 90301.68 | 197232.2
| Storage balance of system | 20586.1 | 45980.25
| Power Equipment | 12171.025 | 12171.025
| Controls & communication | 211.67 | 211.67
| System integration | 18892.74 | 40727.15
| Eng., procurement, construction | 21228.84 | 45509.05
| Project Dev | 26747.72 | 57150.9
| Grid integration | 2116.7 | 2116.7
| Total ESS intalled cost | 156295.3535 | 401098.945
Operating Characteristics
| Via: PNNL paper | Batteries (100 MW)
| resource | LI - LFP | LI - NMC | Vanadium | Lead Acid | PSH
| RTE - ratio of net energy discharged to grid | 86% | 86% | 69% | 82% | 80%
| response time (seconds) | (1-4) | (1-4) | (1-4) | (1-4) | 5 - 500
| Cycle life | 2000 | 1200 | 5201 | 669 | 13870
| Calendar life (yrs) | 10 | 10 | 15 | 12 | 40
| Duration corresponding to cycle life (yrs) | 5.77 | 3.46 | 15 | 1.93 | 40
Misc. Lithium Ion
Operating characteristics
Lithium-ion 100 MW
| inverter loading ratio | 1.3
| inverter size | 2.5MW per inverter
Notes:
Land costs for Lithium Ion captured as fixed cost over time for rental rather than up-front purchase
assumed model baseline 100-MW 1,500 Vdc using 72 cell monocrystalline 19.5% efficient modules

## Pumped Storage Hydro
Source: https://www.pnnl.gov/sites/default/files/media/file/Final%20-%20ESGC%20Cost%20Performance%20Report%2012-11-2020.pdf | [5 empty] | Costs were adjusted to 2020 US dollars (USD) using producer price index data for the electric power distribution industry from the U.S. Bureau of Labor Statistics (BLS) (U.S. BLS, 2020).
Native 2020 $
System Size (MW) | 100 | 100 | 1000 | 1000
Duration (hours) | 4 | 10 | 4 | 10
Cost component | cost ($/kW)
Reservoir construction & infrastructure | 324 | 760 | 272 | 640
Powerhouse construction & infrastructure | 742 | 742 | 623 | 623
Electro/mechanical | 467 | 467 | 392 | 392
Total ESS installed cost | 1533 | 1969 | 1287 | 1655
Total ESS + contigency fee | 2046 | 2623 | 1717 | 2202
Fixed O&M $/kW-yr | 30.4 |  | 17.8
Variable O&M $/MWh | 0.5125 |  | 0.5125
Source: | Table 26 | Table 27
System Size (MW) | 500
Duration (hours) | 10
Cost component | $/kw | $M, 2020 USD
Upper + lower reservoir | 1016 | 457
Tunnels | 163 | 73
Powerhouse excavation | 97 | 42
Powerhouse structure, equip. BOP | 1010 | 454
Total direct costs | 2286 | 1026
EPC management services inc. contingency | 472 | 0.236
Owner's cost | 448 | 0.00448
Proj mgmt & design engineering | 103 | 51
Construction mgmt & startup support | 103 | 51
contingency | 308 | 154
Total indirect cost | 920
Total installed cost | 3206 | 1282
Source: Table 34
Size MW | 100 | 1000
Hours | 10 | 10
Fixed O&M Components | $/kW-yr | $/kW-yr
Labor | 15.7 | 3.1
Parts | 5.6 | 5.6
Refurbishment | 9 | 9
Total Fixed O&M | 30.3 | 17.7
Operating Characteristics
Via: PNNL paper | Batteries (100 MW)
resource | LI - LFP | LI - NMC | Vanadium | Lead Acid | PSH
RTE - ratio of net energy discharged to grid | 86% | 86% | 69% | 82% | 80%
response time (seconds) | (1-4) | (1-4) | (1-4) | (1-4) | 5 - 500
Cycle life | 2000 | 1200 | 5201 | 669 | 13870
Calendar life (yrs) | 10 | 10 | 15 | 12 | 40
Duration corresponding to cycle life (yrs) | 5.77 | 3.46 | 15 | 1.93 | 40

## CCCT
Source: https://www.netl.doe.gov/projects/files/CostAndPerformanceBaselineForFossilEnergyPlantsVol1BitumCoalAndNGtoElectBBRRev4-1_092419.pdf
Case: | B31B | 2X1 CT NGCC w/CO2 Capture | [7 empty] | Case: | B31A | 2X1 CT NGCC w/o CO2 Capture
Plant Size (MW, net): | 646 | 2018 $ | [7 empty] | Plant Size (MW, net): | 727 | 2018 $
Total Plant Cost | [9 empty] | Total Plant Cost
[6 empty] | Contingencies |  | Total Plant Cost | [7 empty] | Contingencies |  | Total Plant Cost
Description | Equipment Cost | Material Cost | Labor | Bare Erected Cost | Engineering CM H.O.& Fee | Process | Project | $/1,000 | $/kW | Description | Equipment Cost | Material Cost | Labor | Bare Erected Cost | Engineering CM H.O.& Fee | Process | Project | $/1,000 | $/kW
Feedwater & Misc. BOP Systems | 43078 | 9208 | 28493 | 80779 | 16156 | 0 | 18296 | 115231 | 178.3762 | Feedwater & Misc. BOP Systems | 36307 | 8124 | 21726 | 66157 | 13231 | 0 | 14788 | 94176 | 129.5406
Flue Gas Cleanup | 174914 | 77111 | 164208 | 416233 | 83247 | 67257 | 113347 | 680084 | 1052.7616 | CT & Accessories | 74850 | 1773 | 5730 | 82353 | 16471 | 0 | 14937 | 113761 | 156.4801
CT & Accessories | 74850 | 1773 | 5730 | 82353 | 16471 | 0 | 14937 | 113761 | 176.1006 | HRSG, Ductwork & Stack | 64630 | 2394 | 16455 | 83479 | 16696 | 0 | 15115 | 115290 | 158.5832
HRSG, Ductwork & Stack | 56467 | 2104 | 14479 | 73050 | 14610 | 0 | 13223 | 100883 | 156.1656 | Steam Turbine & Accessories | 53594 | 1252 | 14990 | 69836 | 13967 | 0 | 12770 | 96573 | 132.8377
Steam Turbine & Accessories | 45220 | 1072 | 12811 | 59103 | 11821 | 0 | 10809 | 81733 | 126.5217 | Cooling Water System | 18087 | 2847 | 7271 | 28205 | 5641 | 0 | 5162 | 39008 | 53.6561
Cooling Water System | 24306 | 3812 | 9784 | 37902 | 7580 | 0 | 6937 | 52419 | 81.144 | Accessory Electric Plant | 17410 | 2624 | 9903 | 29937 | 5987 | 0 | 5409 | 41333 | 56.8542
Accessory Electric Plant | 24650 | 5471 | 18184 | 48305 | 9661 | 0 | 8714 | 66680 | 103.2198 | Instrumentation & Control | 9793 | 448 | 3928 | 14169 | 2834 |  | 2550 | 19553 | 26.8955
Instrumentation & Control | 11347 | 522 | 4538 | 16407 | 3281 | 709 | 3060 | 23457 | 36.3111 | Improvements to Site | 1657 | 2263 | 15412 | 19332 | 3866 | 0 | 4640 | 27838 | 38.2916
Improvements to Site | 1711 | 2338 | 15924 | 19973 | 3995 | 0 | 4794 | 28762 | 44.5232 | Building & Structure | 0 | 6581 | 7506 | 14087 | 2817 | 0 | 2536 | 19440 | 26.74
Building & Structure | 0 | 6254 | 7018 | 13272 | 2654 | 0 | 2389 | 18315 | 28.3514 | Total | 276328 | 28306 | 102921 | 407555 | 81510 | 0 | 77907 | 566972 | 779.879
Total | 456543 | 109665 | 281169 | 847377 | 169476 | 67966 | 196506 | 1281325 | 1983.4752
[10 empty] | Owners Cost | [7 empty] | $/1,000 | $/kW
Owners Cost | [7 empty] | $/1,000 | $/kW | Pre-Production Costs | [7 empty] | 20036 | 27.5598
Pre-Production Costs | [7 empty] | 39833 | 61.661 | Inventory Capital |  |  |  | 566972 |  |  |  | 3134 | 4.3109
Inventory Capital | [7 empty] | 8432 | 13.0526 | Initial Cost for Catalyst & Chemicals | [7 empty] | 847 | 1.1651
Initial Cost for Catalyst & Chemicals | [7 empty] | 847 | 1.3111 | Land | [7 empty] | 300 | 0.41265
Land | [7 empty] | 300 | 0.4644 | Other Owner's Costs | [7 empty] | 85046 | 116.9821
Other Owner's Costs | [7 empty] | 192199 | 297.5217 | Financing Costs | [7 empty] | 15308 | 21.0564
Financing Costs | [7 empty] | 34596 | 53.5542 | Total Overnight Costs | [7 empty] | 691643 | 951.3659
Total Overnight Costs | [7 empty] | 1557532 | 2411.0402 | TASC Multiplier (IOU, 33 year) | [7 empty] | 1.093
TASC Multiplier (IOU, 33 year) | [7 empty] | 1.093 |  | Total As-Spent Cost | [7 empty] | 755965.799 | 1039.8429
Total As-Spent Cost | [7 empty] | 1702382.476 | 2635.267
[10 empty] | Annual Operating & Maintenance Costs | [7 empty] | $ | $/kW-net
Annual Operating & Maintenance Costs | [7 empty] | $ | $/kW-net | Labor | [7 empty] | 8126458 | 11.185
Labor | [7 empty] | 15643360 | 24.955 | Tax + Insurance | [7 empty] | 11339411 | 15.607
Tax + Insurance | [7 empty] | 25626472 | 39.686 | Fixed Operating Costs Total | [7 empty] | 19465869 | 26.792
Fixed Operating Costs Total | [7 empty] | 41269832 | 63.911 | Maintenance Material | [7 empty] | 6463464 | 1.195
Maintenance Material | [7 empty] | 14607089 | 3.038 | Consumables | [7 empty] | 2758905 | 0.51
Consumables | [7 empty] | 12357234 | 2.57 | Waste Disposal | [7 empty] | 2401 | 0.50998
Waste Disposal | [7 empty] | 1235596 | 0.026 | Variable Operating Costs Total | [7 empty] | 9224770 | 1.705
Variable Operating Costs Total | [7 empty] | 27087919 | 5.63 | Fuel Cost | [7 empty] | 152160153 | 28.126
Fuel Cost | [7 empty] | 152160153 | 31.646
ADJUSTED TO 2020 $
Case: | B31B | 2X1 CT NGCC w/CO2 | [7 empty] | Case: | B31A | 2X1 CT NGCC w/o CO2
Plant Size (MW, net): | 646 | [8 empty] | Plant Size (MW, net): | 727
Total Plant Cost | [9 empty] | Total Plant Cost
[6 empty] | Contingencies |  | Total Plant Cost | [7 empty] | Contingencies |  | Total Plant Cost
Description | Equipment Cost | Material Cost | Labor | Bare Erected Cost | Engineering CM H.O.& Fee | Process | Project | $/1,000 | $/kW | Description | Equipment Cost | Material Cost | Labor | Bare Erected Cost | Engineering CM H.O.& Fee | Process | Project | $/1,000 | $/kW
Feedwater & Misc. BOP Systems | 44906.1011 | 9598.7599 | 29702.1574 | 84207.0184 | 16841.6122 | 0 | 19072.4274 | 120121.0579 | 185.9459 | Feedwater & Misc. BOP Systems | 37847.7602 | 8468.7582 | 22647.9863 | 68964.5046 | 13792.4839 | 0 | 15415.5584 | 98172.5469 | 135.0379
Flue Gas Cleanup | 182336.8254 | 80383.3595 | 171176.4949 | 433896.6798 | 86779.7529 | 70111.1853 | 118157.1066 | 708944.7247 | 1097.4377 | CT & Accessories | 78026.4094 | 1848.2408 | 5973.164 | 85847.8143 | 17169.9798 | 0 | 15570.8815 | 118588.6756 | 163.1206
CT & Accessories | 78026.4094 | 1848.2408 | 5973.164 | 85847.8143 | 17169.9798 | 0 | 15570.8815 | 118588.6756 | 183.5738 | HRSG, Ductwork & Stack | 67372.7033 | 2495.5942 | 17153.3008 | 87021.5983 | 17404.5282 | 0 | 15756.4353 | 120182.5617 | 165.313
HRSG, Ductwork & Stack | 58863.2901 | 2193.2874 | 15093.4453 | 76150.0228 | 15230.0046 | 0 | 13784.1445 | 105164.1719 | 162.7928 | Steam Turbine & Accessories | 55868.3686 | 1305.1311 | 15626.1306 | 72799.6303 | 14559.7176 | 0 | 13311.9205 | 100671.2684 | 138.4749
Steam Turbine & Accessories | 47139.0011 | 1117.4925 | 13354.6604 | 61611.154 | 12322.6478 | 0 | 11267.7015 | 85201.5033 | 131.8909 | Cooling Water System | 18854.558 | 2967.8181 | 7579.5594 | 29401.9356 | 5880.3871 | 0 | 5381.0598 | 40663.3825 | 55.9331
Cooling Water System | 25337.4737 | 3973.7698 | 10199.2036 | 39510.4472 | 7901.6725 | 0 | 7231.3855 | 54643.5051 | 84.5875 | Accessory Electric Plant | 18148.8282 | 2735.3547 | 10323.2536 | 31207.4365 | 6241.0703 | 0 | 5638.5417 | 43087.0485 | 59.2669
Accessory Electric Plant | 25696.072 | 5703.1728 | 18955.6744 | 50354.9193 | 10070.9839 | 0 | 9083.796 | 69509.6992 | 107.6002 | Instrumentation & Control | 10208.5855 | 467.0118 | 4094.6925 | 14770.2899 | 2954.2665 | 0 | 2658.2143 | 20382.7707 | 28.0368
Instrumentation & Control | 11828.5326 | 544.1521 | 4730.5791 | 17103.2639 | 3420.2358 | 739.0878 | 3189.8572 | 24452.4447 | 37.8521 | Improvements to Site | 1727.3181 | 2359.0349 | 16066.039 | 20152.3921 | 4030.0614 | 0 | 4836.9077 | 29019.3612 | 39.9166
Improvements to Site | 1783.6097 | 2437.2177 | 16599.7668 | 20820.5942 | 4164.5358 | 0 | 4997.443 | 29982.573 | 46.4127 | Building & Structure | 0 | 6860.2779 | 7824.5321 | 14684.81 | 2936.545 | 0 | 2643.6202 | 20264.9753 | 27.8748
Building & Structure | 0 | 6519.401 | 7315.8229 | 13835.2239 | 2766.6278 | 0 | 2490.382 | 19092.2337 | 29.5545 | Total | 288054.5313 | 29507.2217 | 107288.6585 | 424850.4115 | 84969.0399 | 0 | 81213.1394 | 591032.5908 | 812.9747
Total | 475917.3153 | 114318.8536 | 293100.9689 | 883337.1377 | 176668.053 | 70850.2731 | 204845.1251 | 1335700.589 | 2067.648 | BOP | 68251.4777
[10 empty] | Owners Cost | [7 empty] | $/1,000 | $/kW
Owners Cost | [7 empty] | $/1,000 | $/kW | Pre-Production Costs | [7 empty] | 20886.2677 | 28.7294
Pre-Production Costs | [7 empty] | 41523.393 | 64.2777 | Inventory Capital | [7 empty] | 3266.9976 | 4.4938
Inventory Capital | [7 empty] | 8789.8288 | 13.6065 | Initial Cost for Catalyst & Chemicals | [7 empty] | 882.9441 | 1.2145
Initial Cost for Catalyst & Chemicals | [7 empty] | 882.9441 | 1.3668 | Land | [7 empty] | 312.7311 | 0.43017
Land | [7 empty] | 312.7311 | 0.4841 | Other Owner's Costs | [7 empty] | 88655.0971 | 121.9465
Other Owner's Costs | [7 empty] | 200355.349 | 310.1476 | Financing Costs | [7 empty] | 15957.6256 | 21.95
Financing Costs | [7 empty] | 36064.1505 | 55.8269 | Total Overnight Costs | [7 empty] | 720994.254 | 991.739
Total Overnight Costs | [7 empty] | 1623628.9855 | 2513.3576 | TASC Multiplier (IOU, 33 year) | [7 empty] | 1.1394 | 0
TASC Multiplier (IOU, 33 year) | [7 empty] | 1.1394 | 0 | Total As-Spent Cost | [7 empty] | 788046.7196 | 1083.9707
Total As-Spent Cost | [7 empty] | 1774626.4811 | 2747.0998
[10 empty] | Annual Operating & Maintenance Costs | [7 empty] | $ | $/kW-net
Annual Operating & Maintenance Costs | [7 empty] | $ | $/kW-net | Labor | [7 empty] | 8471320.4981 | 11.6597
Labor | [7 empty] | 16307217.2683 | 26.014 | Tax + Insurance | [7 empty] | 11820621.5846 | 16.2693
Tax + Insurance | [7 empty] | 26713982.5923 | 41.3702 | Fixed Operating Costs Total | [7 empty] | 20291942.0828 | 27.929
Fixed Operating Costs Total | [7 empty] | 43021199.8606 | 66.6232 | Maintenance Material | [7 empty] | 6737754.0218 | 1.2457
Maintenance Material | [7 empty] | 15226970.0359 | 3.1669 | Consumables | [7 empty] | 2875984.6515 | 0.53164
Consumables | [7 empty] | 12881637.9393 | 2.6791 | Waste Disposal | [7 empty] | 2502.8912 | 0.53162
Waste Disposal | [7 empty] | 1288030.9875 | 0.027103 | Variable Operating Costs Total | [7 empty] | 9616241.5645 | 1.7774
Variable Operating Costs Total | [7 empty] | 28237449.0186 | 5.8689 | Fuel Cost | [7 empty] | 158617373.4129 | 29.3196
Fuel Cost | [7 empty] | 158617373.4129 | 32.989
Operating characteristics | Case B31A |  | Case B31B
Steam Cycle, MPa/°C/°C (psig/°F/°F) | 16.4/585/585 (2,378/1,085/1,085) |  | 16.4/585/585 (2,378/1,085/1,085)
Fuel | Natural Gas |  | Natural Gas
Fuel Pressure at Plant Battery Limit MPa (psia) | 3.0 (430) |  | 3.0 (430)
Condenser Pressure, mm Hg (in. Hg) | 50.8 (2) |  | 50.8 (2)
Cooling Water to Condenser, °C (°F) | 16 (60) |  | 16 (60)
Cooling Water from Condenser, °C (°F) | 27 (80) |  | 27 (80)
Stack Temperature, °C (°F) | 82 (181) |  | 31 (87)
SO2 Control | Low Sulfur Fuel |  | Low Sulfur Fuel
NOx Control | LNB and SCR |  | LNB and SCR
SCR Efficiency, %A | 85.4 |  | 86.7
Ammonia Slip (End of Catalyst Life), ppmv | 10 |  | 10
Particulate Control | N/A |  | N/A
Mercury Control | N/A |  | N/A
CO2 Control | N/A |  | Cansolv
Overall Carbon CaptureA | N/A |  | 90%
CO2 Sequestration | N/A |  | Off-site Saline formation
Performance Summary | Case B31A |  | Case B31B
HHV net plant efficiency | 53.6% |  | 47.7%
HHV net plant heat rate, kj/kWh (Btu/kWh) | 6713 (6363) |  | 7,554 (7,159)
HHV Combustion Turbine Efficiency | 35.2% |  | 35.2%
LHV net plant efficiency | 59.4% |  | 52.8%
LHV net plant heat rate, kj/kWh (Btu/kWh) | 6060 (5743) |  | 6,818 (6,462)
LHV Combustion Turbine Efficiency, % | 39% |  | 39%
Steam Turbine Cycle Efficiency, % | 39.7% |  | 46.8%
Steam Turbine Heat Rate, kJ/kWh (Btu/kWh) | 9,074 (8,600) |  | 7,684 (7,283)
Condenser Duty, GJ/hr (MMBtu/hr) | 1,405 (1,332) |  | 832 (788)
AGR Cooling Duty, GJ/hr (MMBtu/hr) | – (–) |  | 1,351 (1,281)
Natural Gas Feed Flow, kg/hr (lb/hr) | 93,272 (205,630) |  | 93,272 (205,630)
HHV Thermal Input, kWt | 1354905 |  | 1354905
LHV Thermal Input, kWt | 1222936 |  | 1222936
Raw Water Withdrawal, (m3/min)/MWnet (gpm/MWnet) | 0.015 (4.0) |  | 0.028 (7.4)
Raw Water Consumption, (m3/min)/MWnet (gpm/MWnet) | 0.012 (3.1) |  | 0.018 (4.8)
Plant Power Summary | Case B31A |  | Case B31B
Combustion Turbine Power, MWe | 477 |  | 477
Steam Turbine Power, MWe | 263 |  | 213
Total Gross Power, MWe | 740 |  | 690
Auxiliary Load Summary
Circulating Water Pumps, kWe | 2810 |  | 4580
Combustion Turbine Auxiliaries, kWe | 1020 |  | 1020
Condensate Pumps, kWe | 150 |  | 170
Cooling Tower Fans, kWe | 1460 |  | 2370
CO2 Capture/Removal Auxiliaries, kWe | 0 |  | 10600
CO2 Compression, kWe | 0 |  | 17090
Feedwater Pumps, kWe | 4830 |  | 4830
Ground Water Pumps, kWe | 260 |  | 430
Miscellaneous Balance of PlantA , kWe | 570 |  | 570
SCR, kWe | 2 |  | 2
Steam Turbine Auxiliaries, kWe | 200 |  | 200
Transformer Losses, kWe | 2250 |  | 2200
Total Auxiliaries, MWe | 14 |  | 44
Net Power, MWe | 727 |  | 646
Air Emissions | Case B31A |  |  | Case B31B
| kg/GJ (lb/MMBtu) | Tonne/year (ton/year)A | kg/MWh (lb/MWh)B | kg/GJ (lb/MMBtu) | Tonne/year (ton/year)A | kg/MWh (lb/MWh)B
SO2 | 0.000 (0.001) | 15 (16) | 0.003 (0.006) | 0.000 (0.000) | 0 (0) | 0.000 (0.000)
NOx | 0.002 (0.004) | 56 (61) | 0.010 (0.022) | 0.001 (0.003) | 51 (56) | 0.010 (0.022)
Particulate | 0.001 (0.002) | 29 (32) | 0.005 (0.012) | 0.000 (0.000) | 0 (0) | 0.000 (0.000)
Hg | 0.00E+0 (0.00E+0) | 0.000 (0.000) | 0.00E+0 (0.00E+0) | 0.00E+0 (0.00E+0) | 0.000 (0.000) | 0.00E+0 (0.00E+0)
CO | 0.001 (0.002) | 29 (32) | 0.005 (0.012) | 0.000 (0.000) | 0 (0) | 0.000 (0.000)
CO2 | 51 (119) | 1,852,253 (2,041,760) | 336 (741) | 5 (12) | 185,225 (204,176) | 36 (80)
CO2C | - | - | 342 (755) | - | - | 39 (85)
Notes
All plants assumed to be located at generic site in midwestern US. Likely need to adjust for area
Gasifier/Boiler tech: HRSG
Missing:
time to full load - zero to full output

## Recip Peaker
Cost Components | $, thousands | Operating Characteristics & Assumptions
Civil/structural/architectural subtotal | 6861 | Configuration | Internal combustion engine 4 * 5.6 MW | Source: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
Engines | 11974 | Combustion Emissions Controls | None | case 4
Mechanical BOP | 5521 | Post-Combustion Emissions Control | SCR | Native 2019 $
Mechanical subtotal | 17495 | Plant Characteristics
Electrical subtotal | 6668 | Net Plant Capacity (60 deg F, 60% RH) | 21.4 MW
Project indirects | 180 | Net Plant Heat Rate, HHV Basis | 8295 Btu/Wh
EPC fee | 1923 | Unavailable: | minimum load heat rate/ turn down, %
EPC subtotal | 33127 | Fuel | NG
Owner's services | 1586 | Assumptions:
Land | 300 | EPC contracting fee | 10%
Owner's fuirnished equipment |  | Project contingency | 8%
Electrical Interconnection | 720 | Owner's services | 7.5%
Gas interconnection | 125 | Estimated land Requirements | 10
Owner's cost subtotal | 14705 | Estimated land cost ($/acre) | 30000
Project contingency | 2869 | Transmission line costs ($/mile) | 720000
Total CAPEX | 38727 | Miles | 1
|  | Substation expansion ($) | 0
Cost |  | Pipeline cost ($/mile) | 100000
Fixed O&M $/kW-yr | 35.16 | miles | 0.5
Variable O&M ($/MWh) | 5.69 | metering station | 75000
|  | Predicted Emissions Rates | lb/MMBtu
|  | Nox - with SCR | 0.02
|  | SO2 | 0
|  | CO | 0.03
|  | CO2 - Per 40 CFR98 Sub Part C | 117
Adjusted to 2020 $
Cost Components | $, thousands
Civil/structural/architectural subtotal | 6996.1617
Engines | 12209.8878
Mechanical BOP | 5629.7637
Mechanical subtotal | 17839.6515
Electrical subtotal | 6799.3596
Project indirects | 183.546
EPC fee | 1960.8831
EPC subtotal | 33779.6019
Owner's services | 1617.2442
Land | 305.91
Owner's fuirnished equipment
Electrical Interconnection | 734.184
Gas interconnection | 127.4625
Owner's cost subtotal | 14994.6885
Project contingency | 2925.5193
Total CAPEX | 39489.9219
Cost
Fixed O&M $/kW-yr | 35.8527
Variable O&M ($/MWh) | 5.8021

## frame peaker
Cost Components | $, thousands | Operating Characteristics & Assumptions |  | Source: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
Civil/structural/architectural subtotal | 12300 | Configuration | Combustion turbine, simple cycle F-class, 233MW | Case 6
Mech. Major equipment | 54000 |  |  | Native 2019 $
Mech. BOP | 17200 | Combustion Emissions Controls | Dry Low Emissions Combustor
Mechanical subtotal | 71200 | Post-Combustion Emissions Control | None
Electrical subtotal | 20200 | Fuel type | NG / No.2 Backup 1 x 237 MW rating
Project indirects | 1900 | Plant Characteristics
EPC fee | 12270 | Net Plant Capacity (60 deg F, 60% RH) | 233 MW
EPC subtotal | 134970 | Net Plant Heat Rate, HHV Basis | 9905 Btu/kWh
Owner's services | 9448
Land | 600 | Assumptions:
Electrical Interconnection | 1200 | EPC contracting fee | 10%
Gas interconnection | 4500 | Project contingency | 10%
Owner's cost subtotal | 15748 | Owner's services | 7%
Project contingency | 15072 | Estimated land Requirements | 20
Total CAPEX | 165790 | Estimated land cost ($/acre) | 30000
|  | Transmission line costs ($/mile) | 1200000
Cost | $ | Miles | 1
Fixed O&M $/kW-yr | 7 | Substation expansion ($) | 0
Variable O&M |  | Pipeline cost ($/mile) | 2800000
Consumables ($/MWh) | 0.6 | miles | 0.5
CT major maintenance ($/Start) | 18500 | metering station | 3100000
|  | Predicted Emissions Rates | lb/MMBtu
|  | NOx | 0.03
|  | SO2 | 0
|  | CO2 | 117
Adjusted to 2020 $
Cost Components | $, thousands
Civil/structural/architectural subtotal | 12542.31
Mech. Major equipment | 55063.8
Mech. BOP | 17538.84
Mechanical subtotal | 72602.64
Electrical subtotal | 20597.94
Project indirects | 1937.43
EPC fee | 12511.719
EPC subtotal | 137628.909
Owner's services | 9634.1256
Land | 611.82
Electrical Interconnection | 1223.64
Gas interconnection | 4588.65
Owner's cost subtotal | 16058.2356
Project contingency | 15368.9184
Total CAPEX | 169056.063
Cost | $
Fixed O&M $/kW-yr | 7.1379
Variable O&M
Consumables ($/MWh) | 0.61182
CT major maintenance ($/Start) | 18864.45

## Biomass
Configuration | 50MW plant | Operating Characteristics |  |  | Source: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
Fuel type | woodchips | Configuration | 50MW plant, Bubbling Fluidized Bed |  | Case 13
Cost component | $ | Combustion Emissions Controls | OFA |  | Native 2019 $
civil/structural/architectural | 22266000 | Post-Combustion Emissions Control | SCR / Baghouse
Mechanical | 88818000 | Plant Characteristics
Electrical | 26608000 | Net Plant Capacity (60 deg F, 60% RH) (MW) | 50
Project indirects | 15418000 | Net Plant Heat Rate, HHV Basis (Btu/kWh) | 13300
EPC fee | 15311000 | Predicted Emissions Rates | lb/MMBtu | Note
EPC subtotal | 168421000 | NOx | 0.08 | NOx removal using OFA, SCR
Owners costs |  | SO2 | <0.03 | SO2 assumed negligable for wood fuel
Owner's services | 11789000 | PM | 0.03 | Controlled using pulse jet fabric filter
Land | 1500000 | CO2 | 206 | Per 40 CFR 98
Electrical Interconnection* | 1200000
Owners cost subtotal | 14489000
Contingency | 21949000
Total CAPEX | 204859000
*assumes 1 mile spur line
Fixed O&M
Labor | 3510000
Materials & contract services | 1250000
Admin & general | 1526000
Fixed O&M subtotal | 6286000
$/kW-yr | 125.72
Variable O&M $/MWh | 4.83
Adjusted to 2020 $
Cost component | $
civil/structural/architectural | 22704640.2
Mechanical | 90567714.6
Electrical | 27132177.6
Project indirects | 15721734.6
EPC fee | 15612626.7
EPC subtotal | 171738893.7
Owners costs | 0
Owner's services | 12021243.3
Land | 1529550
Electrical Interconnection* | 1223640
Owners cost subtotal | 14774433.3
Contingency | 22381395.3
Total CAPEX | 208894722.3
*assumes 1 mile spur line
Fixed O&M
Labor | 3579147
Materials & contract services | 1274625
Admin & general | 1556062.2
Fixed O&M subtotal | 6409834.2
$/kW-yr | 128.1967
Variable O&M $/MWh | 4.9252

## Small Modular Nuclear
Cost Components | thousands $ | Operating Characteristics & Assumptions
Civil/structural/architectural subtotal | 583524 | Configuration: | 12 * 50MW small module reactor plant. 600MW total capacity | Source: https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf
Nuclear island | 648360 | Net Plant Heat Rate, HHV Basis (Btu/kWh) | 10046 | Case 12
Conventional island | 421434 | No regulated emissions to report |  | Native 2019 $
Balance of Plant | 389016 | Assumptions:
Mechanical subtotal | 1458810 | EPC contracting fee | 10% of direct & indirect costs
Electrical subtotal | 259344 | Project contingency | 10% of Project costs
Project indirects | 551000 | Owner's services | 7.5% of project costs
EPC fee | 285267.8 | Estimated land Requirements (acres) | 35
EPC subtotal | 3137945.8 | Estimated land cost ($/acre) | 30000
Owner's services | 235346 | Transmission line costs ($/mile) | 2520000
Land | 1050 | Substation expansion ($) | 0
Electrical Interconnection | 2520
Owner's cost subtotal | 238916
Project contingency | 337686
Total CAPEX | 3714547.8
Cost | $
Fixed O&M $/kW-yr | 95
Variable O&M ($/MWh) | 3
Adjusted to 2020 $
Cost Components | thousands $
Civil/structural/architectural subtotal | 595019.4228
Nuclear island | 661132.692
Conventional island | 429736.2498
Balance of Plant | 396679.6152
Mechanical subtotal | 1487548.557
Electrical subtotal | 264453.0768
Project indirects | 561854.7
EPC fee | 290887.5757
EPC subtotal | 3199763.3323
Owner's services | 239982.3162
Land | 1070.685
Electrical Interconnection | 2569.644
Owner's cost subtotal | 243622.6452
Project contingency | 344338.4142
Total CAPEX | 3787724.3917
Cost | $
Fixed O&M $/kW-yr | 96.8715
Variable O&M ($/MWh) | 3.0591

## CC matrix
Resource |  | CCCT | Frame Peaker | Recip Peaker | pump storage hydro | Battery 2hr | Battery 4 hr | Battery 10 hr | PV + Bat. | PV + B Residential | PV | Onshore wind | Offshore wind | Biomass | Sm Mod Nuclear | CCCT | Frame Peaker | Recip Peaker | pump storage hydro | Battery 2 hour | Battery 4 hour | Battery 10 hour | PV + Bat. | PV + B Residential | PV | Onshore wind | Offshore wind | Biomass | Sm Mod Nuclear
Size (MW) |  | 727 | 233 | 22.4 | 500 | 60 | 100 | 100 | 100MW PV + 60MW Battery | 7kW PV w/ 3-5kW bat. | 100 | 2.6 | 6.1 | 50 | 600 | 727 | 233 | 22.4 | 500 | 60 | 100 | 100 | 100MW PV + 60MW Battery | 7kW PV w/ 3-5kW bat. | 100 | 2.6 | 6.1 | 50 | 600
Component | cost scale | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW | $/kW
Overnight cost
Structural/Equipment |  | 436.8112 | 324.7285 | 1160.9558 | 1144 | 464.9832 | 1026.8438 | 2096.149 | 1027.7878 | 1444.3572 | 504.62 | 1010.5227 | 1326.6297 | 2808.0906 | 991.699 | 40.3% | 44.76% | 65.85% | 44.62% | 56.14% | 65.7% | 52.26% | 53.32% | 32.75% | 45.54% | 69.01% | 31.91% | 67.21% | 15.71%
BOP/BOS |  | 93.881 | 75.274 | 251.3287 | 908 | 134.9522 | 205.861 | 459.8025 | 314.8986 | 1101.7798 | 208.43 | 332.4222 | 2172.9807 | 996.7364 | 661.1327 | 8.661% | 10.37% | 14.26% | 35.41% | 16.29% | 13.17% | 11.46% | 16.34% | 24.98% | 18.81% | 22.7% | 52.27% | 23.86% | 10.47%
eng, procurement & construction |  | 116.8763 | 590.682 | 1508.0179 | 102.472 | 728.5134 | 212.2884 | 455.0905 | 1675.2477 |  | 943.42 |  | #DIV/0! | 3434.7779 | 5332.9389 | 10.78% | 81.41% | 85.54% | 3.997% | 87.95% | 13.58% | 11.35% | 86.9% |  | 85.15% |  | #DIV/0! | 82.21% | 84.48%
financing for overnight |  | 21.95 | [9 empty] | 34.6698 | 186.6051 |  |  | 2.025% | [9 empty] | 2.368% | 4.489%
Land |  | 0.43017 | 2.6258 | 13.6567 |  | 4.9215 | 3.0111 |  |  |  |  | 44.8668 |  | 30.591 | 1.7845 | 0.03968% | 0.3619% | 0% |  | 0.5942% | 0.1927% |  |  |  |  | 3.064% |  | 0.7322% | 0.02827%
Labor |  | 147.5772 |  |  |  | 62.9852 | 47.8683 |  | 163.4981 | 342.8125 | 120.67 |  |  |  |  | 13.61% |  |  |  | 7.604% | 3.063% |  | 8.481% | 7.772% | 10.89%
Other Owner's costs |  | 116.9821 | 49.6633 | 80.3924 | 0.00896 | 16.3442 | 16.3474 |  | 46.7777 |  | 21.94 |  | 148.8762 | 240.4249 | 399.9705 | 10.79% | 6.845% | 4.56% | 0.0003495% | 1.973% | 1.046% |  | 2.427% |  | 1.98% |  | 3.581% | 5.755% | 6.336%
Contingency |  | 107.1623 | 65.961 | 130.6035 | 308 | 22.6544 | 23.1052 |  | 52.1044 |  | 32.91 | 87.6942 | 322.2252 | 447.6279 | 573.8974 | 9.886% | 9.091% | 7.408% | 12.01% | 2.735% | 1.478% |  | 2.703% |  | 2.97% | 5.989% | 7.751% | 10.71% | 9.091%
Interconnection
Substation
Transmission |  |  | 5.2517 | 32.7761 |  | 30.8246 | 21.167 | 21.167 | 40.7288 |  | 21.94 |  | #DIV/0! | 24.4728 | 4.2827 |  | 0.7238% | 1.859% |  | 3.721% | 1.354% | 0.5277% | 2.113% |  | 1.98% |  | #DIV/0! | 0.5858% | 0.06784%
Gas Pipeline |  |  | 19.6938 | 5.6903 | [12 empty] | 2.714% | 0.3228%
Total |  | 1083.9707 | 725.5625 | 1762.9429 | 2564 | 828.3113 | 1562.9535 | 4010.9895 | 1927.7195 | 4410.8019 | 1107.97 | 1464.2892 | 4157.3169 | 4177.8944 | 6312.874 | 1083.9707 | 725.5625 | 1762.9429 | 2564 | 828.3113 | 1562.9535 | 4010.9895 | 1927.7195 | 4410.8019 | 1107.97 | 1464.2892 | 4157.3169 | 4177.8944 | 6312.874
Total 2022 from NREL ATB |  | 1071.2022 | 948.3063 | 1670.7683 | 2656.152 | 777.3852 | 1666.6359 | N/A | 1079.1871 | 2428.1498 | 1306.9477 | 1348.8534 | 4507.0776 | 4464.7799 | N/A
Difference |  | 12.7685 | 222.7438 | 92.1747 | 92.152 | 50.9261 | 103.6823 |  | 848.5324 | 1982.6521 | 198.9777 | 115.4358 | 349.7607 | 286.8855
Fixed O&M ($/kW-yr) |  | 27.929 | 7.1379 | 35.8527 | 24 | [5 empty] | 18.649 |  |  | 128.1967 | 96.8715
Variable O&M ($/MWh) |  | 2.4448 | 0.61182 | 5.8021 | [9 empty] | 4.9252 | 3.0591
Start up Cost |  |  | 18864.45
Operating Characteristics
Key
HAVE DATA
NO DATA
NOT SURE
NOT APPLICABLE

## alt matrix
Overnight cost
Resource | Size (MW) | cost scale | Structural/Equipment | BOP/BOS | eng, procurement & construction | financing for overnight | Land | Labor | Other Owner's costs | AFUDC | Contingency | Substation | Transmission | Gas Pipeline | Total | Total 2022 from NREL ATB | Difference | FOM ($/kW-yr) | VOM ($/MWh) | Start up Cost | Operating Characteristics
CCCT | 727 | $/kW | 436.8112 | 93.881 | 116.8763 | 21.95 | 0.43017 | 147.5772 | 116.9821 |  | 107.1623 |  |  |  | 1083.9707 | 1071.2022 | 12.7685 | 27.929 | 2.4448
Frame Peaker | 233 | $/kW | 324.7285 | 75.274 | 590.682 |  | 2.6258 |  | 49.6633 |  | 65.961 |  | 5.2517 | 19.6938 | 725.5625 | 948.3063 | 222.7438 | 7.1379 | 0.61182 | 18864.45
Recip Peaker | 22.4 | $/kW | 1160.9558 | 251.3287 | 1508.0179 |  | 13.6567 |  | 80.3924 |  | 130.6035 |  | 32.7761 | 5.6903 | 1762.9429 | 1670.7683 | 92.1747 | 35.8527 | 5.8021
pump storage hydro | 500 | $/kW | 1144 | 908 | 102.472 |  |  |  | 0.00896 |  | 308 |  |  |  | 2564 | 2656.152 | 92.152 | 24
Battery 2hr | 60 | $/kW | 464.9832 | 134.9522 | 728.5134 |  | 4.9215 | 62.9852 | 16.3442 |  | 22.6544 |  | 30.8246 |  | 828.3113 | 777.3852 | 50.9261
Battery 4 hr | 100 | $/kW | 1026.8438 | 205.861 | 212.2884 |  | 3.0111 | 47.8683 | 16.3474 |  | 23.1052 |  | 21.167 |  | 1562.9535 | 1666.6359 | 103.6823
Battery 10 hr | 100 | $/kW | 2096.149 | 459.8025 | 455.0905 | [7 empty] | 21.167 |  | 4010.9895 | N/A
PV + Bat. | 100MW PV + 60MW Battery | $/kW | 1027.7878 | 314.8986 | 1675.2477 |  |  | 163.4981 | 46.7777 |  | 52.1044 |  | 40.7288 |  | 1927.7195 | 1079.1871 | 848.5324
PV + B Residential | 7kW PV w/ 3-5kW bat. | $/kW | 1444.3572 | 1101.7798 |  |  |  | 342.8125 | [6 empty] | 3078.1036 | 2428.1498 | 649.9538
PV | 100 | $/kW | 504.62 | 208.43 | 943.42 |  |  | 120.67 | 21.94 |  | 32.91 |  | 21.94 |  | 1107.97 | 1306.9477 | 198.9777 | 18.649
Onshore wind | 2.6 | $/kW | 1010.5227 | 332.4222 |  | 34.6698 | 44.8668 |  |  |  | 87.6942 |  |  |  | 1464.2892 | 1348.8534 | 115.4358
Offshore wind | 6.1 | $/kW | 1326.6297 | 2172.9807 | #DIV/0! | 186.6051 |  |  | 148.8762 |  | 322.2252 |  | #DIV/0! |  | 4157.3169 | 4507.0776 | 349.7607
Biomass | 50 | $/kW | 2808.0906 | 996.7364 | 3434.7779 |  | 30.591 |  | 240.4249 |  | 447.6279 |  | 24.4728 |  | 4177.8944 | 4464.7799 | 286.8855 | 128.1967 | 4.9252
Sm Mod Nuclear | 600 | $/kW | 991.699 | 661.1327 | 5332.9389 |  | 1.7845 |  | 399.9705 |  | 573.8974 |  | 4.2827 |  | 6312.874 | N/A | N/A | 96.8715 | 3.0591
Key
HAVE DATA
NO DATA
NOT SURE
NOT APPLICABLE